SECTION 074210

METAL COMPOSITE MATERIAL PANELS

GENERAL

GENERAL PROVISIONS

Attention is directed to the CONTRACT AND GENERAL CONDITIONS and all Sections within DIVISION 01 - GENERAL REQUIREMENTS which are hereby made a part of this Section of the Specifications.

DESCRIPTION OF WORK

Work Included: Provide labor, materials and equipment necessary to complete the work of this Section, including but not limited to the following:

Metal composite material (MCM) wall [and soffit] panels and attachment systems.

Sustainable Design Intent: Comply with project requirements intended to achieve sustainable design, measured and documented according to the LEED Green Building Rating System, of the US Green Building Council. Refer to Section 018110 - SUSTAINABLE DESIGN REQUIREMENTS for certification level and certification requirements.

Related Work: The following items are not included in this Section and are specified under the designated Sections:

Section 054000 - Cold-Formed Metal Framing for secondary support framing supporting metal panels.

Section 072100 - THERMAL INSULATION for insulation behind metal panels.

Section 076200 - Sheet Metal Flashing and Trim for copings, flashings, and other sheet metal work not part of metal panel assemblies.

Section 079200 - Joint Sealants for field-applied sealants not otherwise specified in this Section.

SUBMITTALS

Product Data: For each type of product.

Include construction details, material descriptions, dimensions of individual components and profiles, and finishes for each type of panel and accessory.

LEED Submittals:

MRc2, Building Product Disclosure and Optimization, Environmental Product Declarations (EPD):

If project needs the product specific EPD for LEED point totals, then delete options for the industry-wide EPDs.

Option 1: For composite metal panel, submit industry-wide (generic) EPDs or product specific Type III EPDs.

Shop Drawings:

Include fabrication and installation layouts of metal composite material panels; details of edge conditions, joints, panel profiles, corners, anchorages, attachment assembly, trim, flashings, closures, and accessories; and special details.

Accessories: Include details of the flashing, trim and anchorage, at a scale of not less than 1-1/2 inches per 12 inches.

Distinguish between factory- and field-assembled work.

Delegated-Design Submittal: For metal panel assembly indicated to comply with performance requirements and design criteria, including analysis data signed and sealed by the qualified professional engineer responsible for their preparation.

Exterior Wall Certification: Submit manufacturer’s certification that exterior wall panels, as designed in the assemblies indicated on the Drawings, has been tested to meet the requirements of NFPA 285 and passed.

Samples for Verification: For each type of exposed finish required, prepared on Samples of size indicated below.

Metal Composite Material Panels: 12 inches long by actual panel width. Include fasteners, closures, and other metal panel accessories.

Include 4-way joint for panels.

Exposed Sealants: For each type and color of joint sealant required. Install joint sealants in 1/2-inch-wide joints formed between two 6-inch-long strips of material matching the appearance of metal panels adjacent to joint sealants.

Qualifications: Qualifications of Professional Engineer and Installer.

Product Test Reports: For each product, tests performed by a qualified testing agency.

Field quality-control reports.

QUALITY ASSURANCE

Engineering Responsibility: Preparation of Shop Drawings, design calculations, and other structural data by a qualified professional engineer.

Professional Engineer Qualifications: A professional engineer who is legally qualified to practice in the state the project is located and who is experienced in providing engineering services of the kind indicated. Engineering services are defined as those performed for installations of panels that are similar to those indicated for this Project in material, design, and extent.

Installer Qualifications: An employer of workers trained and approved by manufacturer.

Installer's responsibilities include fabricating and installing metal panel assemblies and providing professional engineering services needed to assume engineering responsibility.

Fabricator Qualifications: Certified by metal panel manufacturer to fabricate and install manufacturer's wall panel system.

Source Limitations: Obtain each type of metal panel through one source from a single manufacturer.

Fire Test Performance for Exterior Wall: Passes NFPA 285, Standard Fire Test Method for Evaluation of Fire Propagation Characteristics of Exterior Non-Load-Bearing Wall Assemblies Containing Combustible Components.

Preconstruction Compatibility and Adhesion Testing: Submit to joint-sealant manufacturers, for testing indicated below, samples of materials that will contact or affect joint sealants.

Use manufacturer's standard test methods to determine whether priming and other specific joint preparation techniques are required to obtain rapid, optimum adhesion of joint sealants to joint substrates.

Preinstallation Conference: Conduct conference at Project site to comply with requirements in Division 01. Review methods and procedures related to metal panel assemblies including, but not limited to, the following:

Meet with The Owner, Architect, Owner’s insurer if applicable, testing and inspecting agency representative, metal panel Installer, metal panel manufacturer's representative, structural-support Installer, and installers whose work interfaces with or affects metal panels including installers of doors, windows, and louvers.

Review and finalize construction schedule and verify availability of materials, Installer's personnel, equipment, and facilities needed to make progress and avoid delays.

Review methods and procedures related to metal panel installation, including manufacturer's written instructions.

Examine support conditions for compliance with requirements, including alignment between and attachment to structural members.

Review flashings, special siding details, wall penetrations, openings, and condition of other construction that will affect metal panels.

Review governing regulations and requirements for insurance, certificates, and testing and inspecting if applicable.

Review temporary protection requirements for metal panel assembly during and after installation.

Review wall panel observation and repair procedures after metal panel installation.

Document proceedings, including corrective measures and actions required, and furnish copy of record to each participant.

Mockups: Provide mock-ups as specified in Section 014330 - MOCK-UPS, coordinate with other trades as required.

DELIVERY, STORAGE, AND HANDLING

Deliver components, sheets, metal composite material panels, and other manufactured items so as not to be damaged or deformed. Package metal panels for protection during transportation and handling.

Unload, store, and erect metal composite material panels in a manner to prevent bending, warping, twisting, and surface damage.

Store metal composite material panels vertically, covered with suitable weathertight and ventilated covering. Store metal composite material panels to ensure dryness, with positive slope for drainage of water. Do not store metal composite material panels in contact with other materials that might cause staining, denting, or other surface damage.

Do not allow storage space to exceed 120 deg F.

Retain strippable protective covering on metal composite material panels during installation.

PROJECT CONDITIONS

Weather Limitations: Proceed with installation only when existing and forecasted weather conditions permit assembly of metal composite material panels to be performed according to manufacturers' written instructions and warranty requirements.

Field Measurements: Verify locations of structural members and wall opening dimensions by field measurements before metal panel fabrication and indicate measurements on Shop Drawings.

Established Dimensions: Where field measurements cannot be made without delaying the Work, either establish framing and opening dimensions and proceed with fabricating metal panels without field measurements, or allow for field trimming of panels. Coordinate wall construction to ensure that actual building dimensions, locations of structural members, and openings correspond to established dimensions.

COORDINATION

Coordinate metal composite material panel installation with rain drainage work, flashing, trim, and construction of girts, studs, soffits, and other adjoining work to provide a leakproof, secure, and noncorrosive installation.

WARRANTY

Special Warranty: Manufacturer's standard form in which manufacturer agrees to repair or replace components of metal panel assemblies that fail in materials or workmanship within specified warranty period.

Failures include, but are not limited to, the following:

Structural failures, including rupturing, cracking, or puncturing.

Deterioration of metals and other materials beyond normal weathering.

Warranty Period: Two years from date of Substantial Completion.

Special Warranty on Panel Finishes: Manufacturer's standard form in which manufacturer agrees to repair finish or replace metal composite material panels that show evidence of deterioration of factory-applied finishes within specified warranty period.

Fluoropolymer Finish: Deterioration includes, but is not limited to, the following:

Color fading more than 5 Hunter units when tested according to ASTM D 2244.

Chalking in excess of a No. 8 rating when tested according to ASTM D 4214.

Cracking, checking, peeling, or failure of paint to adhere to bare metal.

Finish Warranty Period: 20 years from date of Substantial Completion.

PRODUCTS

PERFORMANCE REQUIREMENTS

Delegated Design: Design metal composite material panel assembly, including comprehensive engineering analysis by a qualified professional engineer, using performance requirements and design criteria indicated.

General: Provide metal composite material panel assemblies that comply with performance requirements specified as determined by testing manufacturers' standard assemblies similar to those indicated for this Project, by a qualified testing and inspecting agency.

Structural Performance: Provide metal composite material panel assemblies capable of withstanding the effects of gravity loads and loads and stresses within limits and under conditions indicated, based on testing according to ASTM E 330.

Wind Loads: As required by Code. [As indicated on Structural Drawings.]

Deflection Limits: Engineer metal wall panel assemblies to withstand test pressures with deflection no greater than 1/180 of the span and no evidence of material failure, structural distress, or permanent deformation exceeding 0.2 percent of the clear span, at code required loading.

Retain "Air Infiltration" and "Water Penetration under Static Pressure" paragraphs below for metal composite material panels that span openings between supports; usually delete for panels mounted on solid substrates.

Air Infiltration: Air leakage of not more than 0.06 cfm/sq. ft. (0.3 L/s per sq. m) when tested according to ASTM E 283 at the following test-pressure difference:

Test-Pressure Difference: 6.24 lbf/sq. ft. (300 Pa).

Water Penetration under Static Pressure: No water penetration when tested according to ASTM E 331 at the following test-pressure difference:

Test-Pressure Difference: 6.24 lbf/sq. ft. (300 Pa).

Thermal Movements: Allow for thermal movements from ambient and surface temperature changes by preventing buckling, opening of joints, overstressing of components, failure of joint sealants, failure of connections, and other detrimental effects. Base calculations on surface temperatures of materials due to both solar heat gain and nighttime-sky heat loss.

Temperature Change (Range): 120 deg F (67 deg C), ambient; 180 deg F (100 deg C), material surfaces.

Retain "Fire-Resistance Ratings" Paragraph below only if products specified are part of a fire-resistance-rated assembly. Indicate rating, testing agency, and testing agency's design designation on Drawings.

Fire-Resistance Ratings: Comply with ASTM E 119; testing by a qualified testing agency. Identify products with appropriate markings of applicable testing agency.

Indicate design designations from UL's "Fire Resistance Directory" or from the listings of another qualified testing agency.

Retain "Fire Propagation Characteristics" Paragraph below if project is required to comply with NFPA 285.

Fire Propagation Characteristics: Metal composite material wall panel system passes NFPA 285 testing.

LEED Requirements:

MRc2, Building Product Disclosure and Optimization, Environmental Product Declarations (EPD):

If project needs the product specific EPD for LEED point totals, then delete options for the industry-wide EPDs.

Option 1: Provide composite metal panels with industry-wide (generic) EPDs or product specific Type III EPDs.

METAL COMPOSITE MATERIAL WALL PANELS

General: Provide factory-formed and -assembled, metal composite material wall panels fabricated from two metal facings that are bonded to a solid, extruded thermoplastic core; formed into profile for installation method indicated. Include attachment assembly components, panel stiffeners, and accessories required for weathertight system.

Aluminum Composite Material Panels: Formed with 0.020-inch- (0.50-mm-) thick, aluminum sheet facings.

The following manufacturers are included because they are part of the industry-wide EPD and have fire retardant cores. Other fabricators may carry these products under their own brands:

If project needs the product specific EPD for LEED point totals, then delete options for the industry-wide EPDs.

Red color text indicates fire-retardant products, if project is required to comply with NFPA 285.

Acceptable Products: Subject to compliance with requirements, provide one of the following products:

3A Composites USA, Inc.; Alucobond Plus (Basis of Design, product specific Type III EPD).

Alcoa Inc.; Reynobond FR.

Alpolic Materials, a division of Mitsubishi; Alpolic/pe Alpolic/fr.

Alucoil North America; Alucoil FR.

Firestone Building Products, LLC; UNA-FAB Series 1500, with fire-rated core.

Panel Thickness: 0.157 inch (4 mm).

Fire-Retardant Core: Noncombustible, with the following surface burning characteristics as determined by testing identical products per ASTM E 84 by UL or another testing and inspection agency acceptable to authorities having jurisdiction.

Flame-Spread Index: 25 or less.

Smoke- Development Index: 450 or less.

Attachment Assembly Components: Formed from extruded aluminum.

Include manufacturer's standard perimeter extrusions, panel stiffeners, panel clips and anchor channels.

Attachment Assembly: Manufacturer's standard rainscreen system.

MISCELLANEOUS MATERIALS AND ACCESSORIES

Miscellaneous Metal Subframing and Furring: ASTM C 645, cold-formed, metallic-coated steel sheet ASTM A 653/A 653M, G90 (Z275 hot-dip galvanized) coating designation or ASTM A 792/A 792M, Class AZ50 (Class AZM150) aluminum-zinc-alloy coating designation unless otherwise indicated. Provide manufacturer's standard sections as required for support and alignment of metal composite material panel system.

Panel Accessories: Provide components required for a complete, weathertight panel system including trim, copings, fasciae, mullions, sills, corner units, clips, flashings, sealants, gaskets, fillers, closure strips, and similar items. Match material and finish of metal composite material panels unless otherwise indicated.

Flashing and Trim: Provide flashing and trim formed from same material as metal composite material panels as required to seal against weather and to provide finished appearance. Locations include, but are not limited to, bases, drips, sills, jambs, corners, endwalls, framed openings, rakes, fasciae, parapet caps, soffits, reveals, and fillers.

Match material, finish, and color as facings of adjacent panels, unless otherwise indicated.

Panel Fasteners: Self-tapping screws designed to withstand design loads. Provide exposed fasteners with heads matching color of metal composite material panels by means of plastic caps or factory-applied coating. Provide EPDM or PVC sealing washers for exposed fasteners.

Panel Sealants: ASTM C 920; elastomeric polyurethane or silicone sealant; of type, grade, class, and use classifications required to seal joints in metal composite material panels and remain weathertight; and as recommended in writing by metal composite material panel manufacturer.

Comply with requirements of Section 079200 - Joint Sealants.

RAINSCREEN ATTACHMENT SYSTEM

Z-Shaped Furring: With slotted or nonslotted web, face flange of 1-1/4 inches wall attachment flange of 7/8 inch, minimum bare metal thickness of 0.0179 inch and depth required to fit insulation thickness indicated.

Rainscreen System: Provide system that has been tested in accordance with AAMA 508 (Pressure Equalized Rain Screen Wall Cladding Test) – Standard Test Method for Water Penetration of Exterior Vented Rainscreen Panel System. The test requires a minimum airflow of 1 CFM / SF of weather wall area through the vented rainscreen system to replicate severe storm and imperfection in air/vapor barrier system. While maintaining 1 CFM/SF airflow, the system must be able to pressure equalize and sustain zero pressure difference between the interior and exterior wall cavity without any water penetration.

Available Manufacturers: Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

Universe Systems, Division of Universe Corporation.

LYMO Architectural Panel Systems Inc.

POHL Inc. of America.

Centria Architectural Systems.

Metal Sales & Service, Inc.

Rout and return wall panel system with dry joints for rainscreen assembly.

FABRICATION

General: Fabricate and finish metal composite material panels and accessories at the factory, by manufacturer's standard procedures and processes, as necessary to fulfill indicated performance requirements demonstrated by laboratory testing. Comply with indicated profiles and with dimensional and structural requirements.

Factory form panels with sharply cut edges, with no displacement of face sheets or protrusion of core material.

Fabricate panels with panel stiffeners, as required to comply with deflection limits, attached to back of panels with structural silicone sealant or bond tape.

Dimensional Tolerances:

Length: Plus 0.375 inch.

Width: Plus 0.188 inch.

Thickness: Plus or minus 0.008 inch.

Panel Bow: 0.8 percent maximum of panel length or width.

Squareness: 0.2 inch maximum.

Sheet Metal Flashing and Trim: Fabricate flashing and trim to comply with manufacturer's recommendations and recommendations in SMACNA's "Architectural Sheet Metal Manual" that apply to design, dimensions, metal, and other characteristics of item indicated.

Form exposed sheet metal accessories that are without excessive oil canning, buckling, and tool marks and that are true to line and levels indicated, with exposed edges folded back to form hems.

Seams for Aluminum: Fabricate nonmoving seams with flat-lock seams. Form seams and seal with epoxy seam sealer. Rivet joints for additional strength.

Seams for Other Than Aluminum: Fabricate nonmoving seams in accessories with flat-lock seams. Tin edges to be seamed, form seams, and solder.

Sealed Joints: Form nonexpansion but movable joints in metal to accommodate elastomeric sealant to comply with SMACNA standards.

Conceal fasteners and expansion provisions where possible. Exposed fasteners are not allowed on faces of accessories exposed to view.

Fabricate cleats and attachment devices from same material as accessory being anchored or from compatible, noncorrosive metal recommended by metal panel manufacturer.

Size: As recommended by SMACNA's "Architectural Sheet Metal Manual" or metal panel manufacturer for application but not less than thickness of metal being secured.

FINISHES

Comply with NAAMM's "Metal Finishes Manual for Architectural and Metal Products" for recommendations for applying and designating finishes.

Finish designations prefixed by AA comply with the system established by the Aluminum Association for designating aluminum finishes.

Protect mechanical and painted finishes on exposed surfaces from damage by applying a strippable, temporary protective covering before shipping.

Appearance of Finished Work: Variations in appearance of abutting or adjacent pieces are acceptable if they are within one-half of the range of approved Samples. Noticeable variations in the same piece are not acceptable. Variations in appearance of other components are acceptable if they are within the range of approved Samples and are assembled or installed to minimize contrast.

Select one of the following finish types, listed in order of relative cost, high-to-low:

High-Performance Organic Finish (3-Coat Fluoropolymer):  AA-C12C40R1x (Chemical Finish:  cleaned with inhibited chemicals; Chemical Finish:  conversion coating; Organic Coating:  manufacturer's standard 3-coat, thermocured system consisting of specially formulated inhibitive primer, fluoropolymer color coat, and clear fluoropolymer topcoat, with both color coat and clear topcoat containing not less than 70 percent polyvinylidene fluoride resin by weight).  Prepare, pretreat, and apply coating to exposed metal surfaces to comply with AAMA 2605 and with coating and resin manufacturers' written instructions.

[Metallic]Color and Gloss:  As selected by Architect from manufacturer's full range.

High-Performance Organic Finish (2-Coat Fluoropolymer Mica Finish System):  AA-C12C40R1x (Chemical Finish:  cleaned with inhibited chemicals; Chemical Finish:  conversion coating; Organic Coating:  manufacturer's standard two-coat, thermocured system consisting of specially formulated inhibitive primer and fluoropolymer color coat, with color coat containing mica and not less than 70 percent polyvinylidene fluoride resin by weight, with a minimum total dry film thickness of 1.2 mil).  Prepare, pretreat, and apply coating to exposed metal surfaces to comply with AAMA 2605 and with coating and resin manufacturers' written instructions.

Metallic Color and Gloss:  As selected by Architect from manufacturer's full range.

High-Performance Organic Finish (2-Coat Fluoropolymer):  AA-C12C40R1x (Chemical Finish:  cleaned with inhibited chemicals; Chemical Finish:  conversion coating; Organic Coating:  manufacturer's standard 2-coat, thermocured system consisting of specially formulated inhibitive primer and fluoropolymer color coat, with color coat containing not less than 70 percent polyvinylidene fluoride resin by weight).  Prepare, pretreat, and apply coating to exposed metal surfaces to comply with AAMA 2605 and with coating and resin manufacturers' written instructions.

[Non-metallic]Color and Gloss:  As selected by Architect from manufacturer's full range.

Clear anodized finish is least expensive, but also the least consistent finish.

Clear Anodic Finish: AAMA 611, AA-M12C22A41, Class I, 0.018 mm or thicker.

EXECUTION

EXAMINATION

Examine substrates, areas, and conditions, with Installer present, for compliance with requirements for installation tolerances, metal composite material panel supports, and other conditions affecting performance of the Work.

Examine wall framing to verify that girts, angles, channels, studs, and other structural panel support members and anchorage have been installed within alignment tolerances required by metal composite material panel manufacturer.

Examine wall sheathing to verify that sheathing joints are supported by framing or blocking and that installation is within flatness tolerances required by metal composite material panel manufacturer.

Verify that air- or water-resistive barriers have been installed over sheathing or backing substrate to prevent air infiltration or water penetration.

For the record, prepare written report, endorsed by Installer, listing conditions detrimental to performance of work.

Examine roughing-in for components and assemblies penetrating metal composite material panels to verify actual locations of penetrations relative to seam locations of metal composite material panels before installation.

Proceed with installation only after unsatisfactory conditions have been corrected.

PREPARATION

Miscellaneous Supports: Install subframing, furring, and other miscellaneous panel support members and anchorages according to ASTM C 754 and metal composite material panel manufacturer's written recommendations.

METAL COMPOSITE MATERIAL PANEL INSTALLATION

General: Install metal composite material panels according to manufacturer's written instructions in orientation, sizes, and locations indicated on Drawings. Install panels perpendicular to supports unless otherwise indicated. Anchor metal composite material panels and other components of the Work securely in place, with provisions for thermal and structural movement.

Field cutting of metal panels is not permitted.

Flash and seal metal composite material panels at perimeter of all openings. Fasten with self-tapping screws. Do not begin installation until air- or water-resistive barriers and flashings that will be concealed by metal composite material panels are installed.

Install screw fasteners in predrilled holes.

Locate and space fastenings in uniform vertical and horizontal alignment.

Install flashing and trim as metal composite material panel work proceeds.

Locate panel splices over, but not attached to, structural supports. Stagger panel splices and end laps to avoid a four-panel lap splice condition.

Align bottoms of metal composite material panels and fasten with blind rivets, bolts, or self-tapping screws. Fasten flashings and trim around openings and similar elements with self-tapping screws.

Provide weathertight escutcheons for pipe- and conduit-penetrating panels.

Fasteners, Aluminum Panels: Use aluminum or stainless-steel fasteners for surfaces exposed to the exterior; use aluminum or galvanized steel fasteners for surfaces exposed to the interior.

Metal Protection: Where dissimilar metals contact each other or corrosive substrates, protect against galvanic action as recommended in writing by metal composite material panel manufacturer.

Attachment Assembly, General: Install attachment assembly required to support metal composite material wall panels and to provide a complete weathertight wall system, including subgirts, perimeter extrusions, tracks, drainage channels, panel clips, and anchor channels.

Include attachment to supports, panel-to-panel joinery, panel-to-dissimilar-material joinery, and panel-system joint seals.

Do not begin installation until weather barrier and flashings that will be concealed by metal panels are installed.

Rainscreen Installation: Install using manufacturer's standard assembly with vertical channel that provides support and secondary drainage assembly, draining at base of wall. Notch vertical channel to receive support pins. Install vertical channels supported by channel brackets or adjuster angles and at locations, spacings, and with fasteners recommended by manufacturer. Attach metal composite material wall panels by inserting horizontal support pins into notches in vertical channels and into flanges of panels. Leave horizontal and vertical joints with open reveal.

Install wall panels to allow individual panels to be installed and removed without disturbing adjacent panels.

Do not apply sealants to joints unless otherwise indicated.

ACCESSORY INSTALLATION

Accessories, General: Install accessories with positive anchorage to building and weathertight mounting and provide for thermal expansion. Coordinate installation with flashings and other components.

Install components required for a complete metal composite material panel assembly including trim, copings, corners, seam covers, flashings, sealants, gaskets, fillers, closure strips, and similar items. Provide types indicated by metal composite material panel manufacturer; or, if not indicated, provide types recommended in writing by metal composite material panel manufacturer.

Flashing and Trim: Comply with performance requirements, manufacturer's written installation instructions, and SMACNA's "Architectural Sheet Metal Manual." Provide concealed fasteners where possible, and set units true to line and level as indicated. Install work with laps, joints, and seams that will be permanently watertight and weather resistant.

Install exposed flashing and trim that is without excessive oil canning, buckling, and tool marks and that is true to line and levels indicated, with exposed edges folded back to form hems. Install sheet metal flashing and trim to fit substrates and to result in waterproof and weather-resistant performance.

Expansion Provisions: Provide for thermal expansion of exposed flashing and trim. Space movement joints at a maximum of 10 feet (3 m) with no joints allowed within 24 inches (605 mm) of corner or intersection. Where lapped expansion provisions cannot be used or would not be sufficiently waterproof, form expansion joints of intermeshing hooked flanges, not less than 1 inch (25 mm) deep, filled with mastic sealant (concealed within joints).

ERECTION TOLERANCES

Installation Tolerances: Shim and align metal composite material wall panel units within installed tolerance of 1/4 inch in 20 feet (6 mm in 6 m), non-accumulative, on level, plumb, and location lines as indicated, and within 1/8-inch (3-mm) offset of adjoining faces and of alignment of matching profiles.

FIELD QUALITY CONTROL

Testing Agency: Engage a qualified independent testing and inspecting agency to perform field tests and inspections and to prepare test reports.

Water-Spray Test: After installation, test area of assembly as directed by Architect for water penetration according to AAMA 501.2.

Manufacturer's Field Service: Engage a factory-authorized service representative to test and inspect completed metal panel installation, including accessories.

Remove and replace metal panels where tests and inspections indicate that they do not comply with specified requirements.

Additional testing and inspecting, at Contractor's expense, will be performed to determine compliance of replaced or additional work with specified requirements.

Prepare test and inspection reports.

CLEANING AND PROTECTION

Remove temporary protective coverings and strippable films, if any, as metal composite material panels are installed, unless otherwise indicated in manufacturer's written installation instructions. On completion of metal composite material panel installation, clean finished surfaces as recommended by metal composite material panel manufacturer. Maintain in a clean condition during construction.

After metal composite material panel installation, clear weep holes and drainage channels of obstructions, dirt, and sealant.

Replace metal composite material panels that have been damaged or have deteriorated beyond successful repair by finish touchup or similar minor repair procedures.

END OF SECTION